## Sheet1
ALL SMOKE ALARMS SHALL BE CEILING MOUNTED |  | YEAR BUILT or SUBSTANTIALLY MODIFIED
| Before 1975 | 1975 - 8/27/97 | 8/27/97 - 2007 | 1/08 - 2/11 | 2/11 - Present
SMOKE ALARM POWER = | BATTERY or | HARDWIRED, | HARDWIRED, | HARDWIRED, | HARDWIRED,
| HARDWIRED | INTERCONNECTED | INTERCONNECTED | INTERCONNECTED | INTERCONNECTED
|  |  | W/ BATTERY B/U | W/ BATTERY B/U | W/ BATTERY B/U
TYPE OF SMOKE ALARM ( Photoelectric or Ionization)
On the same level, If a required detector is More Than 20 ft. from a kitchen or full bathroom doorway it shall be: | Either: a Dual Detector* OR One Photoelectric AND One Ionization alarm | Photoelectric OR Ionization | Photoelectric OR Ionization | Photoelectric OR Dual Detector* | Photoelectric Only
On the same level, If a required detector is Within 20 ft. of kitchen or full bathroom doorway it shall be: | Photoelectric Only | Photoelectric OR Ionization | Photoelectric Only | Photoelectric Only | Photoelectric Only
Carbon Monoxide detectors:
Shall be located on each habitable level including; in the hallway Outside each separate Sleeping Area (bedrooms), no farther than 10 ft. from any bedroom door.
Carbon Monoxide (CO) Alarm Power Supply
Battery or Plug-In w/battery backup | Allowed | Allowed | Allowed | NOT Allowed | NOT Allowed
Hardwired, interconnected w/battery backup | Allowed | Allowed | Allowed | Required | Required
Alarm Locations
Finished Basement at base of stairs | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO
Unfinished Basement | Smoke | Smoke | Smoke | Smoke & CO | Smoke & CO
Base of Stairs leading to Occupied floor above | Smoke | Smoke | Smoke | Smoke | Smoke
Outside each Sleeping Area (in hallway) | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO
Inside every Bedroom |  |  | Smoke | Smoke | Smoke
Finished Attic (Habitable) | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO | Smoke & CO
Garage (Attached) |  |  |  | Heat Detector | Heat Detector
*A Dual Detector consists of one detector with both photoelectric and ionization technology
One Smoke Alarm is needed for each 1,200 square feet of area, per floor
Low Voltage fire warning systems are exempt from the dual detector technology requirement
Combination Smoke and Carbon Monoxide Alarms MUST have a Voice Feature