## general_report
Uponor North America
Displaying 6 issues at 07/Nov/11 11:13 AM.
Issue Type | Key | Summary | Notes for Technical Bulletin | Status | Resolution | Created | Updated | Fix Version/s
Task | CCN-7 | Siemans CO2/VOC Sensor EOL | Database has been modified to support the AERASGARD RLQ-CO2 / VOC sensor. IE: The VOC AIC has been inverted | Closed | Fixed | 2009-10-07 09:36 | 2011-10-31 17:53 | 44.00.00
Bug | CCN-25 | sometimes DER's do not correctly update under the DSM RTR during installation | Default Databases have cleared Datalinks that contain no data. This should allow datalinks to connect properly at commissioning. | Closed | Fixed | 2010-03-03 17:11 | 2011-10-31 15:26 | 44.00.00
Improvement | CCN-40 | Create clean default data bases for all controllers | Created Default DB process to clear Datalinks and network numbers | Closed | Fixed | 2010-09-21 12:12 | 2011-10-31 15:28 | 44.00.00
Bug | CCN-87 | WM1 Icons for Air Cooling not displayed correctly for Air Zones that share an Air Handler. | Fixed Air Cooling Icon display on the thermostat when using Dampers connected to a common AirHandler | Closed | Fixed | 2011-07-14 17:18 | 2011-11-02 12:44 | 44.00.00
Bug | CCN-46 | Snowmelt Slab Sensor AIC is pointed to Delta 10K curve. Mamac needs to be on the J curve AIC | Update the Snowmelt Slab sensor to work with a more accurate conversion table (AIC): 10K J curve | Closed | Fixed | 2011-01-05 12:00 | 2011-11-02 13:17 | 44.00.00
Improvement | CCN-96 | Change outdoor sensor to Teal AIC | Update the outdoor sensor Conversion table to match the sensor manufacturer. Will improve accuracy around 0C/32F. | Closed | Fixed | 2011-10-31 10:37 | 2011-11-02 13:03 | 44.00.00
Generated at Mon Nov 07 11:13:27 CST 2011 by Logan Grauer using JIRA 4.3.4#620-r152668.